## FIRE FLOW WORKSHEET
SCOPE
This worksheet shall be submitted through ProjectDox for all applicable permits and approved by Hillsboro Fire & Rescue prior to permit issuance. For assistance completing the form, contact the Fire Prevention Division at 503-615-6746. (OFC 507.3)
SECTION 1 - Preparer Information
a. | Preparer Name: | [7 empty] | Date:
| Phone: |  |  | E-mail:
SECTION 2 - General Building Information
a. | Project Name:
Project Address:
b. | Construction Type: | Type IA and IB
c. | Total Fire Flow Calculation Bldg Area: |  |  |  | 1 | sq ft (OFC B104.1)
| Required Fire Flow | 1500 | GPM (based amount without reductions)
d. | Type of Occupancy or Use of Building:
SECTION 3 - Reduction Fire Flow
| Is the building equiped with an approved automatic sprinkler system, installed in accordance with OFC B105.2 as amended by City of Hillsboro HMC 11.28.010? | [8 empty] | Yes | 1500 | GPM
A maximum of a 50% reduction is allowed for an approved automatic sprinkler system, installed in accordance with Oregon Structural Specialty Code 903.3.1.1 and 903.3.1.2. Resulting fire flow shall be no less than 1500 gallons per minute at 20 pounds per square inch. Table B105.2 as amended by City of Hillsboro HMC 11.28.10
SECTION 4 - Minimum Number of Fire Hydrants Required
Refer to Table C102.1 below (2022 Oregon Fire Code, Appendix C) for the minimum number of hydrants required.
[6 empty] | Required Fire Flow: |  |  |  |  | 1500 | GPM
[7 empty] | Required Fire Hydrants: |  |  |  | 1
TABLE C102.1 NUMBER AND DISTRIBUTION OF FIRE HYDRANTS h
| FIRE-FLOW REQUIREMENT (gpm) | MINIMUM NUMBER OF HYDRANTS |  | AVERAGE SPACING BETWEEN HYDRANTS a, b, c, f, g (feet) |  |  | MAXIMUM DISTANCE FROM ANY POINT ON THE STREET OR ROAD FRONTAGE TO A HYDRANT d, f, g
| 1,750 or less | 1 |  | 500 |  |  | 250
| 1,751-2,250 | 2 |  | 450 |  |  | 225
| 2,251-2,750 | 3 |  | 450 |  |  | 225
| 2,751-3,250 | 3 |  | 400 |  |  | 225
| 3,251-4,000 | 4 |  | 350 |  |  | 210
| 4,001-5,000 | 5 |  | 300 |  |  | 180
| 5,001-5,500 | 6 |  | 300 |  |  | 180
| 5,501-6,000 | 6 |  | 250 |  |  | 150
| 6,001-7,000 | 7 |  | 250 |  |  | 150
| 7,001 or more | 8 or more e |  | 200 |  |  | 120
For SI: 304.8 mm, 1 gallon per minute= 3.785 L/m.
a. Reduce by 100 feet for dead-end streets or roads.
b. Hydrants shall be required on both sides of the public streets with an average spacing of 500 feet on each side of the street and be arranged on an alternating basis whenever one or more of the following conditions exist: 1) Streets have median center dividers that make access to hydrants difficult, cause time delay, or create undue hazard. 2) When there are four or more lanes of traffic. 3) The existing street will be widened or have a median center divider in the future, pursuant to the city Transportation System Plan.
c. Where new water mains are extended along streets where hydrants are not needed for protection of structure or similar fire problems, fire hydrants shall be provided at spacing not to exceed 1,000 feet to provide for transportation hazards.
d. Reduce by 50 feet for dead-end streets or roads.
e. One hydrant for each 1,000 gallons per minute or fraction thereof.
f. A 50-percent spacing increase shall be permitted where the building is equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.1 of the International Fire Code.
g. A 25-percent spacing increase shall be permitted where the building is equipped throughout with an approved automatic sprinkler system in accordance with Section 903.3.1.2 or 903.3.1.3 of the International Fire Code or Section P2904 of the International Residential Code.
h. The fire code official is authorized to modify the location, number and distribution of fire hydrants based on site-specific constraints and hazards.
SECTION 5 - Available Fire Flow to the Building
Manually enter available fire flow data calculated to 20 psi. Please attach documentation of the flow test report issued by the water purveyor and/or a calculated available water supply curve graph. The report must include date, time and location of static/residual and flow hydrants, as well as the tester’s name, phone number and address. Flow tests valid for 1 year from date of test.
[8 empty] | Enter FlowTest Results: |  |  |  | GPM
Fire Flow and Hydrant Worksheet

## INSTRUCTIONS
Scope
The following outlines the procedure for determining required fire flow using the Fire Flow and Hydrant Worksheet. The calculations are derived from the 2022 Oregon Fire Code Appendix B and Appendix C, as amended by the City of Hillsboro HMC 11.28.010.
Definitions
Fire Flow. The flow rate of a water supply, measured at 20 pounds per square inch (psi) (138 kPa) residual pressure, that is available for fire fighting.
SECTION 1 - Preparer Information
a. | Preparer Information - enter the name and contact information of the person preparing the form.
SECTION 2 - General Building Information
a. | Project Information - enter the name and address of the project.
b. | Construction Type - choose a construction type from the drop-down menu.
Type IA and Type IB construction. The fire-flow calculation area of Type IA and Type IB construction buildings shall be the area of the three largest successive floors. Exception: Fire-flow calculation area for open parking garages shall be determined by the area of the largest single floor.
c. | Total Bldg Area, Total Fire Area and Bldg Fire Flow - enter the total building area and total fire area
(Bldg Fire Flow will be calculated automatically).
Area separation. Portions of buildings which are separated by fire walls, constructed in accordance with the International Building Code, may be considered separate fire flow calculation areas.
d. | Type of Occupancy or Use of Building - enter the occupancy type or building use.
SECTION 3 - Reduction of Fire Flow
As approved, a reduction of up to 50 percent in required fire flow is allowed when the building is provided with an approved automatic sprinkler system, installed in accordance with NFPA 13 or NFPA 13R. The resulting fire flow must not be less than 1,500 GPM.
SECTION 4 - Minimum Number of Fire Hydrants Required
Refer to OFC Table C102.1 for the minimum number and spacing of hydrants.
SECTION 5 - Available Fire Flow
Enter the available fire flow to the site as indicated by a recent hydrant flow test. The fire flow must be the flow available at 20 psi residual pressure.
Fire Flow and Hydrant Worksheet Instructions

## CONSTRUCTION TYPES
Type IA and IB | GPM | Type IIA and IIIA | GPM
1 | 1500 | 1 | 1500
22701 | 1750 | 12701 | 1750
30201 | 2000 | 17001 | 2000
38701 | 2250 | 21801 | 2250
48301 | 2500 | 24201 | 2500
59001 | 2750 | 33201 | 2750
70901 | 3000 | 39701 | 3000
83701 | 3250 | 47101 | 3250
97701 | 3500 | 54901 | 3500
112701 | 3750 | 63401 | 3750
128701 | 4000 | 72401 | 4000
145901 | 4250 | 82101 | 4250
164201 | 4500 | 92401 | 4500
183401 | 4750 | 103101 | 4750
203701 | 5000 | 114601 | 5000
225201 | 5250 | 126701 | 5250
247701 | 5500 | 139401 | 5500
271201 | 5750 | 152601 | 5750
295901 | 6000 | 166501 | 6000
| 6250 |  | 6250
| 6500 |  | 6500
| 6750 |  | 6750
| 7000 |  | 7000
| 7250 |  | 7250
| 7500 |  | 7500
| 7750 |  | 7750
| 8000 |  | 8000
Type IV and V-A | GPM | Type IIB and IIIB | GPM
1 | 1500 | 1 | 1500
8201 | 1750 | 5901 | 1750
10901 | 2000 | 7901 | 2000
12901 | 2250 | 9801 | 2250
17401 | 2500 | 12601 | 2500
21301 | 2750 | 15401 | 2750
25501 | 3000 | 18401 | 3000
30101 | 3250 | 21801 | 3250
35201 | 3500 | 25901 | 3500
40601 | 3750 | 29301 | 3750
46401 | 4000 | 33501 | 4000
52501 | 4250 | 37901 | 4250
59101 | 4500 | 42701 | 4500
66001 | 4750 | 47701 | 4750
73301 | 5000 | 53001 | 5000
81101 | 5250 | 58601 | 5250
89201 | 5500 | 65401 | 5500
97701 | 5750 | 70601 | 5750
106501 | 6000 | 77001 | 6000
115801 | 6250 | 83701 | 6250
125501 | 6500 | 90601 | 6500
135501 | 6750 | 97901 | 6750
145801 | 7000 | 106801 | 7000
156701 | 7250 | 113201 | 7250
167901 | 7500 | 121301 | 7500
179401 | 7750 | 129601 | 7750
191401 | 8000 | 138301 | 8000
Type V-B | GPM
1 | 1500
3601 | 1750
4801 | 2000
6201 | 2250
7701 | 2500
9401 | 2750
11301 | 3000
13401 | 3250
15601 | 3500
18001 | 3750
20601 | 4000
23301 | 4250
26301 | 4500
29301 | 4750
32601 | 5000
36001 | 5250
39601 | 5500
43401 | 5750
47401 | 6000
51501 | 6250
55701 | 6500
60201 | 6750
64801 | 7000
69601 | 7250
74601 | 7500
79801 | 7750
85101 | 8000
Yes
No